## Base case builds
IA builds to add in the base case (and the project case) -- DISIS-2023-001, 03 CENTRAL, Table 5
Area = expected from the TO; confirm against the case (rerun z6_poi_distance.py -- it now prints each POI bus's area).
# | GEN number | Cluster | Nearest town / county | State | TO at POI | Area (expected from TO) | Area name | POI bus | POI bus name | kV | Substation | Generation type | Service type | Capacity MW | Max summer MW | In-service date | COD | Closest study project | Nodes | ¦Z¦ pu | Why modelled | SantaFe nodes | SantaFe ¦Z¦ pu | EastFork nodes | EastFork ¦Z¦ pu | IronStar nodes | IronStar ¦Z¦ pu | EmpirePrairie nodes | EmpirePrairie ¦Z¦ pu
1 | GEN-2023-173 | DISIS-2023-001 | Kearny | KS | SUNC | 534 | SUNC | 531449 | HOLCOMB7 | 345 | Holcomb 345 kV | Wind | ER/NR | 100 | 100 | 1/9/2027 | 12/31/2029 | SantaFe | 2 | 0.0234 | <=6 nodes | 2 | 0.0234 | 4 | 0.16 | 5 | 0.0448 | 13 | 0.2764
2 | GEN-2023-172 | DISIS-2023-001 | Kearny | KS | SUNC | 534 | SUNC | 531449 | HOLCOMB7 | 345 | Holcomb 345 kV | Wind | ER/NR | 200 | 200 | 1/9/2027 | 12/31/2029 | SantaFe | 2 | 0.0234 | <=6 nodes | 2 | 0.0234 | 4 | 0.16 | 5 | 0.0448 | 13 | 0.2764
3 | GEN-2023-107 | DISIS-2023-001 | Finney/Kearny | KS | SUNC | 534 | SUNC | 531465 | SETAB 7 | 345 | Setab 345 kV | Wind | ER | 300 | 300 | 1/5/2030 | 12/31/2030 | SantaFe | 3 | 0.0427 | <=6 nodes | 3 | 0.0427 | 3 | 0.1407 | 6 | 0.0641 | 12 | 0.2957
4 | GEN-2023-099 | DISIS-2023-001 | Jackson | KS | WERE | 536 | WERE | 532766 | JEC N 7 | 345 | Jeffery Energy Center 345 kV | Solar | ER | 300 | 300 | 8/30/2030 | 12/31/2030 | EmpirePrairie | 5 | 0.0606 | <=6 nodes | 10 | 0.1996 | 15 | 0.383 | 8 | 0.1782 | 5 | 0.0606
5 | GEN-2023-171 | DISIS-2023-001 | Jackson | MO | INDN | 545 | INDN | 548814 | SUB M-161 | 161 | Sub M 161 kV | Battery/Storage | ER/NR | 150 | 150 | 1/2/2028 | 1/6/2028 | EmpirePrairie | 5 | 0.1364 | <=6 nodes | 17 | 0.3571 | 18 | 0.5287 | 16 | 0.3357 | 5 | 0.1364
6 | GEN-2023-033 | DISIS-2023-001 | Clay | MO | WERE | 536 | WERE | 541248 | LBRTYST5 | 161 | Liberty South 161 kV | Battery/Storage | ER/NR | 200 | 200 | 4/15/2028 | 1/7/2028 | EmpirePrairie | 6 | 0.1391 | <=6 nodes | 18 | 0.3598 | 19 | 0.5314 | 17 | 0.3384 | 6 | 0.1391
7 | GEN-2023-170 | DISIS-2023-001 | Chariton | MO | WERE | 536 | WERE | 543062 | SALSBRY5 | 161 | Salisbury 161 kV | Battery/Storage | ER | 150 | 150 | 1/2/2028 | 1/6/2028 | EmpirePrairie | 7 | 0.1798 | added (7 nodes) | 18 | 0.381 | 20 | 0.5643 | 16 | 0.3596 | 7 | 0.1798
TOTAL
Green = within 6 nodes of that project. Yellow row = added beyond the 6-node rule.
Left out: GEN-2023-037 Nearman, GEN-2023-034 Clear Water-Waco, GEN-2023-061 Carthage (>= 7 nodes and >= 0.18 pu from every project).