## README
SMIB PLANT MODEL ¦ INPUT WORKBOOK
PSS/E (.raw, .dyr) and PSCAD (.pscx) models of a plant from one workbook -- smib_build.py, 2026-10-15
HOW TO USE
Step 1 | Fill in the yellow cells -- the example plant (100 MW PV + 100 MW BESS on one MPT) shows the format. A blank cell takes its default (Input_Reference lists every one).
Step 2 | Plant: Model type -- SMIB: each generator one machine on its own equivalent feeder ¦ DETAILED: every feeder section, the units at each node a machine of their own. PSS/E and PSCAD are built alike.
Step 3 | Save, then run: python smib_build.py <this workbook>.xlsx (or keep the workbook next to the script and run the script on its own).
Step 4 | Read <name>_REPORT.txt in the output folder: the equivalents, the load flow, the models and every CHECK line.
SHEETS
Plant | model name and type, bases, POI and grid, gen-tie, operating point, plant controller, PSCAD | input
MPT | main power transformers, 2 or 3 windings | input
Generators | one row per generator: units, GSU, collector, Q control, dynamic and PSCAD models | input
Feeders | the collector feeders, section by section | input
Cables | cable data per length | input
Collectors | collector systems shared by several generators | input
Loads_Shunts | auxiliary loads, capacitor banks, reactors | input
Machines | DETAILED: each machine's own Pgen, P and Q limits, MBASE and ID | input
Bus_Numbers | bus numbers and names of your own (blank = automatic) | input
Dyr_Params | any dynamic model parameter, by generator, model and name | input
Dyr_Records | .dyr records of your own (vendor models) | input
PSCAD_Params | the vendor PSCAD model's parameters, by generator | input
Input_Reference | every input: what it is, its unit, the default when blank, the choices, which model uses it | reference
Dynamic_Models | every dynamic model's parameters: position, default and meaning | reference
COLOURS
your inputs
note | what to enter, the default when blank
Column | column titles
SECTION | a group of items
PSS/E + PSCAD | which model an input goes into
GUIDE
SMIB INPUT | Fill in the sheets, save, then run: python smib_build.py <this workbook>.xlsx
It writes the PSS/E model (.raw rev 33 and .dyr; with PSS/E found, a solved .sav and a flat-run check) and the PSCAD build script (run it where PSCAD 5 and its Python automation library mhi.pscad are: it builds the .pscx), with a report of every equivalent, the load flow and anything to check.
Blank cells take the default in the column note (row 2 of each sheet). Any row whose first cell starts with # is skipped (row 2 is one).
BUSES | Name a bus by its role: POI ¦ HV (the gen-tie's end; the POI when there is no gen-tie) ¦ <MPT> or <MPT>:LV ¦ <MPT>:TV (3-winding) ¦ <MPT>:HV (an MPT with a tie of its own) ¦ <shared collector> (its far end) ¦ <generator>:MV (GSU HV side) ¦ <generator> or <generator>:LV (terminal) ¦ IB (infinite bus). Numbers are automatic from First bus number; Bus_Numbers sets any one.
Plant | Bases, the POI, the grid (SCR and X/R, or short-circuit MVA, or R/X), the gen-tie, the operating point, the plant controller and the PSCAD run settings.
MODEL TYPE | Plant: Model type sets PSS/E and PSCAD alike. SMIB (default): each generator is one machine behind one GSU on a collector equivalent of its own (WECC, each feeder weighed by its MW) from its MPT winding. DETAILED: every feeder section is a branch (identical feeder copies lumped), the units of a generator at each node a machine of their own behind their own GSU; a generator's Dyr_Params, Dyr_Records and PSCAD_Params rows apply to all its machines.
Control mode Q: the plant holds the POI voltage with Q at POI into the grid; PF: with that power factor; V: the plant holds the POI voltage with the infinite bus at Grid voltage. The infinite-bus voltage (and the generators' Q) come out of the load flow.
Plant controller (PSS/E .dyr): REPC_A = a REPCA1 on each generator, each holding the POI; REPC_B = one controller for the whole plant (hybrid PV + BESS): PLNTBU1 at the POI, and on each generator a REAX4BU1 that takes its share of the plant's Q (Qmax / sum of Qmax) and P (Pmax / sum of Pmax). REGC_A / REPC_A records: standard = REGCA1 / REPCA1 from the PSS/E library; USRMDL = REGCAU1 / REPCAU1.
MPT | One row per main power transformer; HV winding first. Three windings: TV kV, the three impedances and their bases. Parallel units: identical units in parallel. Tie: a line of its own from HV to it.
Generators | One row per generator (PV, BESS, wind, synchronous ...): the units (count and one unit's data; the model is their aggregate), its GSU (one GSU's data and the count), its collector (FEEDERS: the WECC equivalent of its rows in Feeders; EQUIVALENT: R X B given; NONE), how it shares the POI's Q, its electrical control model in the .dyr (REEC_A: REECA1, PV and wind; REEC_C: REECCU1, BESS; REEC_D: REECDU1, PV, BESS and WT4) and its PSCAD model (vendor library and definition, or blank for a voltage source at the solved terminal voltage: a network check against PSS/E) and where the inverter connects (LV or MV side of the GSU).
Feeders | The collector feeders section by section from the collector bus out: cable, length and the units tapped at the section's far end. A daisy chain needs no From section; a lateral names the section it leaves from (its far end); 0 = straight from the collector bus. Copies: identical feeders. WECC equivalent: Zeq = sum(Zi Wi^2) / W^2, Beq = sum(Bi), Wi = MW of the units downstream of section i. R ohm, X ohm, B uS: a section's own values (its parallel cables together) in place of Cable x Length -- the GUI's Fill R, X, B from cables shows them to change; Clear R, X, B goes back. A section with R and X needs no cable.
Cables | Cable data per length (R, X in ohm; C in uF or B in uS) and the length unit they are per.
Collectors | Collector systems shared by more than one generator: name and the bus it starts from. Their Feeders rows say whose units each section carries (Units of); the generators on it Connect to its name.
Loads_Shunts | Auxiliary loads (constant impedance, MW and MVAr at 1 pu) and shunts (MVAr at 1 pu: + capacitor, - reactor) on any bus.
Machines | DETAILED model only: a machine's own Pgen, Pmax, Pmin, Qmax, Qmin, fixed Q, MBASE and ID in place of its share of its generator's (the GUI's 'List the DETAILED machines' fills in their names and values). Scale up (GUI) or --scale: a test plant -- MPTs (copies of the first, with its generators), feeders per MPT, GSUs per feeder and inverters per GSU.
Bus_Numbers | Bus numbers or names of your own, by role (the report lists every role and its number).
Dyr_Params | Any parameter of the WECC-approved generic models, by generator, model and PSS/E name or position (ICON2, CON14) -- IB for the infinite bus, PLANT for the plant controller. Inverters: REGCA1 (REGC_A) + REECA1 / REECCU1 / REECDU1 (REEC_A / C / D) + REPCA1 (REPC_A) or REAX4BU1 (with PLNTBU1, REPC_B); WT3: + WTDTA1 WTARA1 WTPTA1 WTTQA1; SYNC: GENROU SEXS TGOV1. REECCU1, REECDU1, PLNTBU1, REAX4BU1 (and REGCAU1, REPCAU1) are user models: the WECC user-model DLL must be loaded for the PSS/E check (ADDLIB_IDV / DLLS in the script). The report lists every model's parameters with the values used. In the GUI, the Dyr_Params tab shows every model's parameters with the values the .dyr gets, a column per generator: double-click one to change it (it becomes a row here), clear it to go back to the default.
Dyr_Records | Records of your own (vendor or user models), one per row, ending in /. {BUS} {ID} {MBASE} {POI} {IB} {HV} {MV} and {<bus role>} are filled in. Type USER generators have only these. Models in user DLLs: list the DLLs in DLLS in the script for the PSS/E check.
PSCAD_Params | Parameters of each generator's vendor PSCAD model (UDM), as PSCAD takes them. Filled in for each inverter it stands for (DETAILED: each node): {UNITS} units, {MVA} their MVA, {P_MW} {Q_MVAR} their P and Q where it connects, {P_PU} {Q_PU} on {MVA}, {UNIT_MVA} {UNIT_P_MW} {UNIT_Q_MVAR} one unit's, {V_PU} {V_KV} {KV} {ANGLE} the voltage there, its base and PSCAD angle, {P_INV_MW} {Q_INV_MVAR} {V_INV_PU} at the inverters' own terminals (a UDM on the MV side), {FREQ} -- e.g. Ninv = {UNITS}, Vt0 = {V_PU}.
PSCAD | The .pscx is built in the same run when PSCAD 5 and its Python library mhi.pscad (pip install mhi.pscad) are on the PC; otherwise run <name>_build_pscad.py where they are. The case holds the grid (source and Thevenin impedance), the gen-tie, the MPTs, each collector (the WECC equivalent as a pi section, or DETAILED: every feeder section, identical feeder copies lumped), the GSUs and, on each GSU's LV side, the inverter: your UDM (PSCAD library, definition and AC port in Generators) or a stand-in source at the solved voltage -- delete it and wire your UDM in its place (the report and the build log list every inverter node). Or take the UDM from the OEM's PSCAD model: Generators, Pick UDM from OEM model -- the model's definitions are listed (their ports, parameters and the IDs of the ones placed in it); the one picked is added to the case's definitions (with the ones it uses and the model's resources, .lib / .obj) and put at every GSU of that generator (every machine of the DETAILED model), PSCAD_Params rows ({UNITS}, {P_PU} ...) set on each; or, with a component ID, that placed one is copied instead, its settings and all. PSCAD inverter at MV: for a UDM with its GSU inside, the inverter on the GSU's HV side and no GSU drawn. It is drawn as a single-line diagram with wires, left to right from the grid; where PSCAD's R, L and C are single-phase, each is drawn three times between breakouts.

## Plant
Item | Value | Unit | Blank means | Choices | Description | Used by
MODEL
Name | Hybrid_PV100_BESS100 |  |  |  | model name: file names and the PSCAD case (letters, digits, _) | PSS/E + PSCAD
Model type | SMIB |  | SMIB | SMIB ¦ DETAILED | SMIB: each generator one machine behind one GSU on its own equivalent feeder (WECC) from its MPT ¦ DETAILED: every feeder section, the units at each node a machine of their own behind their own GSU -- PSS/E and PSCAD alike (blank = SMIB) | PSS/E + PSCAD
System base | 100 | MVA | 100 |  | PSS/E system base (blank = 100) | PSS/E + PSCAD
Build PSS/E .raw | YES |  | YES | YES ¦ NO | YES = the load-flow case (blank = YES) | PSS/E + PSCAD
Build PSS/E .dyr | YES |  | YES | YES ¦ NO | YES = the dynamic models (blank = YES) | PSS/E + PSCAD
Build PSCAD model | YES |  | YES | YES ¦ NO | YES = the PSCAD build script, its data and the .pscx (blank = YES) | PSS/E + PSCAD
Frequency | 60 | Hz | 60 |  | blank = 60 | PSS/E + PSCAD
First bus number | 1000 |  |  |  | buses are numbered from here + 1 (Bus_Numbers sets any one) | PSS/E + PSCAD
POI AND GRID (the infinite bus behind its Thevenin impedance)
POI kV | 230 | kV | required |  |  | PSS/E + PSCAD
POI name | POI |  |  |  | 12 characters at most | PSS/E + PSCAD
Grid SCR | 3 |  | one of SCR, short-circuit MVA or R + X |  | short-circuit ratio at the POI, on the SCR base | PSS/E + PSCAD
Grid X/R | 10 |  |  |  |  | PSS/E + PSCAD
SCR base |  | MW | the generators' Pmax |  | blank = the generators' Pmax | PSS/E + PSCAD
Grid short-circuit MVA |  | MVA |  |  | instead of the SCR (with Grid X/R) | PSS/E + PSCAD
Grid R |  | pu |  |  | instead of the SCR: Thevenin R on the system base | PSS/E + PSCAD
Grid X |  | pu |  |  | instead of the SCR: Thevenin X on the system base | PSS/E + PSCAD
GEN-TIE (POI to the HV bus; blank = none)
Gen-tie length | 5 |  | no gen-tie (the MPTs on the POI bus |  | POI to the substation HV bus; blank = no gen-tie (the MPTs on the POI bus) | PSS/E + PSCAD
Gen-tie length unit | km |  | km | km ¦ mi ¦ kft ¦ m ¦ ft | km, mi, kft, m, ft (blank = km) | PSS/E + PSCAD
Gen-tie values per | km |  | the Gen-tie length unit | km ¦ mi ¦ kft ¦ m ¦ ft | the length R, X, B, C below are per: km, mi, kft, m, ft (blank = the Gen-tie length unit) | PSS/E + PSCAD
Gen-tie R per length | 0.072 | ohm | a typical overhead line of the POI kV |  | one circuit (blank = a typical overhead line of the POI kV) | PSS/E + PSCAD
Gen-tie X per length | 0.495 | ohm | typical |  | one circuit (blank = typical) | PSS/E + PSCAD
Gen-tie B per length | 3.35 | uS | typical |  | one circuit, total charging (blank = typical) | PSS/E + PSCAD
Gen-tie C per length |  | uF |  |  | instead of B | PSS/E + PSCAD
Gen-tie R total |  | ohm |  |  | instead of per length (one circuit) | PSS/E + PSCAD
Gen-tie X total |  | ohm |  |  |  | PSS/E + PSCAD
Gen-tie B total |  | uS |  |  |  | PSS/E + PSCAD
Gen-tie circuits | 1 |  | 1 |  | identical circuits in parallel (blank = 1) | PSS/E + PSCAD
Gen-tie rating | 400 | MVA | typical for the POI kV |  | one circuit (blank = typical for the POI kV) | PSS/E + PSCAD
OPERATING POINT (the load flow's targets at the POI)
Control mode | Q |  |  | Q ¦ PF ¦ V | Q: Q at the POI ¦ PF: power factor at the POI ¦ V: the plant holds the POI voltage with the grid at Grid voltage | PSS/E + PSCAD
POI voltage | 1 | pu | 1.0 |  | the POI voltage the plant holds (blank = 1.0) | PSS/E + PSCAD
Q at POI | 0 | MVAr | 0 |  | mode Q; + = into the grid (blank = 0) | PSS/E + PSCAD
PF at POI | 1 |  |  |  | mode PF; + lagging (Q into the grid), - leading | PSS/E + PSCAD
Grid voltage | 1 | pu | 1.0 |  | mode V: the infinite bus (blank = 1.0) | PSS/E + PSCAD
P at POI |  | MW | each generator at its dispatch |  | blank = each generator at its dispatch ¦ a value = the dispatches scaled to deliver it | PSS/E + PSCAD
PLANT CONTROLLER (PSS/E .dyr)
Plant controller | REPC_B |  | REPC_A | REPC_A ¦ REPC_B | PSS/E .dyr -- REPC_A: a REPCA1 on each generator ¦ REPC_B: one for the plant, PLNTBU1 at the POI and a REAX4BU1 on each generator (hybrid plants) (blank = REPC_A) | PSS/E .dyr
REGC_A / REPC_A records | standard |  | standard | standard ¦ USRMDL | standard: REGCA1 / REPCA1 (PSS/E library) ¦ USRMDL: REGCAU1 / REPCAU1 (the WECC user-model DLL) (blank = standard) | PSS/E .dyr
PSCAD RUN
PSCAD time step | 10 | us | 10 (the vendor model's own requirement wins |  | blank = 10 (the vendor model's own requirement wins) | PSCAD
PSCAD duration | 5 | s | 5 |  | blank = 5 | PSCAD
PSCAD plot step | 100 | us | 100 |  | blank = 100 | PSCAD
PSCAD meter at POI | YES |  |  | YES ¦ NO | YES = a multimeter between the grid and the POI | PSCAD
PSCAD lines as | PI |  | PI | PI ¦ RLC | PI = the gen-tie, each collector and each feeder section one Coupled PI Section (R, X, B in pu, its charging inside); RLC = an R and an L, the charging a C at each end (blank = PI) | PSCAD
PSCAD FAULT AT THE POI
PSCAD fault at POI | YES |  |  | YES ¦ NO | YES = a fault on the grid side of the POI with its timed fault logic, as vendors' test cases have | PSCAD
PSCAD fault time |  | s | 100: none in the run |  | when the fault starts (blank = 100: none in the run) | PSCAD
PSCAD fault duration | 0.15 | s | 0.15 |  | blank = 0.15 | PSCAD
PSCAD fault type | ABCG |  | ABCG | ABCG ¦ ABC ¦ AG ¦ BG ¦ CG ¦ ABG ¦ BCG ¦ ACG ¦ AB ¦ BC ¦ AC | the phases faulted, G = to ground (blank = ABCG) | PSCAD
PSCAD fault resistance | 0.01 | ohm | 0.01 |  | blank = 0.01 | PSCAD
PSCAD LIBRARIES
PSCAD libraries |  |  |  |  | user-model libraries (.pslx) to load, separated by ; | PSCAD

## MPT
Name | HV kV | LV kV | TV kV | MVA | LV MVA | TV MVA | Z HV-LV % | Z HV-TV % | Z LV-TV % | Z HV-LV base MVA | Z HV-TV base MVA | Z LV-TV base MVA | X/R | Load loss kW | Vector group | HV tap | Parallel units | No-load loss % | Magnetising current % | Rating MVA | Tie length | Tie length unit | Tie values per | Tie R per length | Tie X per length | Tie B per length | Tie rating MVA
# MPT name. Its buses: <name> or <name>:LV (LV winding), <name>:TV (tertiary) |  |  | tertiary / 2nd LV winding; blank = two windings | the rating (3 windings: HV winding) | 3 windings | 3 windings | on its base MVA | 3 windings | 3 windings | blank = MVA | blank = MVA | blank = MVA | each impedance | 2 windings, at MVA: instead of X/R | YNd1, YNd11, Dyn1, YNyn0, YNd1d1 ... | HV winding ratio, 1.025 = +2.5 % (blank = 1) | identical units (blank = 1) | of MVA (blank = 0) | of MVA (blank = 0) | blank = MVA | a line of its own from HV to this MPT (blank = none) |  | the length R, X, B are per (blank = Tie length unit) | ohm (blank = a typical overhead line of the HV kV) | ohm (blank = typical) | uS (blank = typical) | blank = typical
MPT1 | 230 | 34.5 |  | 225 |  |  | 10 | [5 empty] | 45 |  | YNd1 | 1 | 1 |  |  | 225

## Generators
Name | Type | Machine ID | Connect to | Units | Unit MVA | Unit Pmax MW | Unit Pmin MW | Unit Qmax MVAr | Unit Qmin MVAr | Unit PF | Terminal kV | Dispatch MW | Q mode | Fixed Q MVAr | Fixed PF | GSU count | GSU MVA | GSU HV kV | GSU LV kV | GSU Z % | GSU X/R | GSU vector group | GSU HV tap | Collector | Collector R | Collector X | Collector B | Collector units | ZSORCE X pu | WMOD | Electrical control | PSCAD library | PSCAD definition | PSCAD AC port | PSCAD source case | PSCAD component ID | PSCAD inverter at
# generator name. Its buses: <name>:MV (GSU HV), <name> or <name>:LV (terminal) | PV BESS WT4 WT3 SYNC USER (USER: Dyr_Records only) | blank = 1 | the bus its collector starts from: MPT1 (LV), MPT1:TV, a shared collector, HV, POI | number of units | one unit (blank = from P and Q) |  | BESS charging: negative (blank = 0) | blank = from Unit PF | blank = -Qmax | Q at Pmax when Qmax is blank (blank = 0.95) | blank = GSU LV kV | this generator's total; blank = Pmax (BESS charging: negative) | share: holds the POI with the other share generators ¦ fixed: its own Q | Q mode fixed (blank = 0) | Q mode fixed, instead of Fixed Q (+ lagging) | blank = Units | one GSU; blank = no GSU (units on the MV bus) |  |  | on GSU MVA |  |  | blank = 1 | FEEDERS: WECC equivalent of its Feeders rows ¦ EQUIVALENT: R X B here ¦ NONE | EQUIVALENT | EQUIVALENT | EQUIVALENT, total charging | pu: system base at collector kV ¦ ohm: R X in ohm, B in uS | on MBASE (blank: inverters 9999, SYNC X''d) | blank: inverters 1, SYNC 0 | PSS/E .dyr -- REEC_A: PV, WT ¦ REEC_C: BESS ¦ REEC_D: PV, BESS, WT4 (blank = REEC_A, BESS REEC_C) | vendor library .pslx (blank = none) | vendor model, library:name (blank = a source: network check) | its AC port (blank = its 3-phase port) | the OEM's PSCAD model (.pscx / .pslx) the UDM comes from: its PSCAD definition added to the case (GUI: Pick UDM from OEM model) | a UDM placed in the source case: copied with its settings instead (blank = the definition, its values from PSCAD_Params) | LV: the inverter (your UDM or the stand-in source) on the GSU's LV side, the GSU built ¦ MV: on its HV side, for a UDM with its GSU inside (blank = LV)
PV | PV | 1 | MPT1 | 25 | 4.2 | 4 | 0 | 1.28 | -1.28 |  | 0.63 |  | share |  |  |  | 4.2 | 34.5 | 0.63 | 6.5 | 8 | YNd1 |  | FEEDERS | [6 empty] | REEC_A | [5 empty] | LV
BESS | BESS | 1 | MPT1 | 25 | 4.4 | 4 | -4 | 1.83 | -1.83 |  | 0.69 |  | share |  |  |  | 4.4 | 34.5 | 0.69 | 6 | 7 | YNd1 |  | FEEDERS | [6 empty] | REEC_C | [5 empty] | LV

## Feeders
Collector | Feeder | Copies | Section | From section | Cable | Length | Length unit | Units at end | Units of | Parallel cables | R ohm | X ohm | B uS
# the generator (its own collector) or a shared collector | feeder name | identical feeders (blank = 1) | 1, 2, 3 ... from the collector bus out | blank = the one before (daisy chain) ¦ 0 = the collector bus ¦ n = a lateral off the end of section n | from Cables |  | blank = km | units tapped at the far end | shared collectors: whose units (repeat the section for another generator's) | blank = 1 | the section's R, its parallel cables together (blank = Cable x Length) | the section's X (blank = Cable x Length) | the section's charging B, total (blank = Cable x Length)
PV | F | 5 | 1 |  | 1000AL | 1.6 | km | 0
PV | F | 5 | 2 |  | 500AL | 0.4 | km | 1
PV | F | 5 | 3 |  | 500AL | 0.4 | km | 1
PV | F | 5 | 4 |  | 4/0AL | 0.4 | km | 1
PV | F | 5 | 5 |  | 4/0AL | 0.4 | km | 1
PV | F | 5 | 6 |  | 1/0AL | 0.4 | km | 1
BESS | F | 5 | 1 |  | 1000AL | 0.8 | km | 0
BESS | F | 5 | 2 |  | 500AL | 0.15 | km | 1
BESS | F | 5 | 3 |  | 500AL | 0.15 | km | 1
BESS | F | 5 | 4 |  | 4/0AL | 0.15 | km | 1
BESS | F | 5 | 5 |  | 4/0AL | 0.15 | km | 1
BESS | F | 5 | 6 |  | 1/0AL | 0.15 | km | 1

## Cables
Cable | Length unit | R per length | X per length | C per length | B per length
# cable type | the values are per | ohm, at operating temperature | ohm | uF | uS, instead of C
1000AL | km | 0.046 | 0.105 | 0.39
500AL | km | 0.09 | 0.118 | 0.3
4/0AL | km | 0.201 | 0.133 | 0.22
1/0AL | km | 0.404 | 0.148 | 0.17

## Collectors
Name | Connect to
# shared collector: its far-end bus has this name | the bus it starts from (MPT1, MPT1:TV ...)

## Loads_Shunts
Kind | At bus | MW | MVAr | Name
# LOAD: constant impedance ¦ SHUNT: + capacitor, - reactor | POI, HV, MPT1, MPT1:TV, PV:MV, PV ... | LOAD, at 1 pu | at 1 pu: LOAD + inductive ¦ SHUNT + capacitive
LOAD | MPT1 | 1 | 0.3 | AUX

## Machines
Machine | Machine ID | Pgen MW | Pmax MW | Pmin MW | Qmax MVAr | Qmin MVAr | Fixed Q MVAr | MBASE MVA
# DETAILED model: a machine, <generator>_<feeder>_S<section> (the GUI lists them); its values in place of its share of its generator's | blank = its generator's | its dispatch (blank = its share of its generator's Dispatch MW) | blank = its units x Unit Pmax | blank = its units x Unit Pmin | blank = its units x Unit Qmax | blank = its units x Unit Qmin | a value: this Q, fixed (blank = as its generator's Q mode) | blank = its units x Unit MVA

## Bus_Numbers
Bus | Number | Name
# its role: IB, POI, HV, MPT1:LV, PV:MV, PV:LV ... | blank = automatic | blank = automatic (12 characters at most)
IB
POI
HV
MPT1:LV
PV:MV
PV:LV
BESS:MV
BESS:LV

## Dyr_Params
Generator | Model | Parameter | Value
# IB: the infinite bus ¦ PLANT: the plant controller (REPC_B) | REGCA1 (REGCAU1) ¦ REECA1 REECCU1 REECDU1 ¦ REPCA1 (REPCAU1) or REAX4BU1 ¦ PLANT: PLNTBU1 ¦ WT3: + WTDTA1 WTARA1 WTPTA1 WTTQA1 ¦ SYNC: GENROU SEXS TGOV1 ¦ IB: GENCLS | PSS/E name (the report lists them all) or position: ICON2, CON14
PLANT | PLNTBU1 | Kp | 1
BESS | REECCU1 | SOCini | 0.5

## Dyr_Records
Generator | Record
# blank = the plant | .dyr text ending in / -- {BUS} {ID} {MBASE} {POI} {IB} {HV} {MV} {<bus role>} are filled in
#PV | {BUS} 'USRMDL' {ID} 'MYMODEL' 101 0 1 3 2 1 1 0.02 0.5 1.0 / <- a row starting with # is skipped

## PSCAD_Params
Generator | Parameter | Value
# | the vendor model's parameter name | as PSCAD takes it (0.63 [kV], 40, {UNITS}, {P_PU} ...)
#PV | Ninv | {UNITS}
#PV | Vt0 | {V_PU} [pu]

## Input_Reference
INPUT REFERENCE ¦ every input of every sheet
What each input is, its unit, what a blank cell means, the choices and which model it goes into. Bus names and the PSCAD placeholders are at the end.
Sheet | Field | Key | Unit | Blank means | Choices | Description | Used by
Plant
Plant | Name | name |  |  |  | model name: file names and the PSCAD case (letters, digits, _) | PSS/E + PSCAD
Plant | Model type | model_type |  | SMIB | SMIB ¦ DETAILED | SMIB: each generator one machine behind one GSU on its own equivalent feeder (WECC) from its MPT ¦ DETAILED: every feeder section, the units at each node a machine of their own behind their own GSU -- PSS/E and PSCAD alike (blank = SMIB) | PSS/E + PSCAD
Plant | System base | sbase_mva | MVA | 100 |  | PSS/E system base (blank = 100) | PSS/E + PSCAD
Plant | Build PSS/E .raw | out_raw |  | YES | YES ¦ NO | YES = the load-flow case (blank = YES) | PSS/E + PSCAD
Plant | Build PSS/E .dyr | out_dyr |  | YES | YES ¦ NO | YES = the dynamic models (blank = YES) | PSS/E + PSCAD
Plant | Build PSCAD model | out_pscad |  | YES | YES ¦ NO | YES = the PSCAD build script, its data and the .pscx (blank = YES) | PSS/E + PSCAD
Plant | Frequency | freq_hz | Hz | 60 |  | blank = 60 | PSS/E + PSCAD
Plant | First bus number | first_bus |  |  |  | buses are numbered from here + 1 (Bus_Numbers sets any one) | PSS/E + PSCAD
Plant | POI kV | poi_kv | kV | required |  |  | PSS/E + PSCAD
Plant | POI name | poi_name |  |  |  | 12 characters at most | PSS/E + PSCAD
Plant | Grid SCR | grid_scr |  |  |  | short-circuit ratio at the POI, on the SCR base | PSS/E + PSCAD
Plant | Grid X/R | grid_x_r |  |  |  |  | PSS/E + PSCAD
Plant | SCR base | scr_base_mw | MW | the generators' Pmax |  | blank = the generators' Pmax | PSS/E + PSCAD
Plant | Grid short-circuit MVA | grid_sc_mva | MVA |  |  | instead of the SCR (with Grid X/R) | PSS/E + PSCAD
Plant | Grid R | grid_r_pu | pu |  |  | instead of the SCR: Thevenin R on the system base | PSS/E + PSCAD
Plant | Grid X | grid_x_pu | pu |  |  | instead of the SCR: Thevenin X on the system base | PSS/E + PSCAD
Plant | Gen-tie length | tie_length |  | no gen-tie (the MPTs on the POI bus |  | POI to the substation HV bus; blank = no gen-tie (the MPTs on the POI bus) | PSS/E + PSCAD
Plant | Gen-tie length unit | tie_unit |  | km | km ¦ mi ¦ kft ¦ m ¦ ft | km, mi, kft, m, ft (blank = km) | PSS/E + PSCAD
Plant | Gen-tie values per | tie_per_unit |  | the Gen-tie length unit | km ¦ mi ¦ kft ¦ m ¦ ft | the length R, X, B, C below are per: km, mi, kft, m, ft (blank = the Gen-tie length unit) | PSS/E + PSCAD
Plant | Gen-tie R per length | tie_r_per | ohm | a typical overhead line of the POI kV |  | one circuit (blank = a typical overhead line of the POI kV) | PSS/E + PSCAD
Plant | Gen-tie X per length | tie_x_per | ohm | typical |  | one circuit (blank = typical) | PSS/E + PSCAD
Plant | Gen-tie B per length | tie_b_per | uS | typical |  | one circuit, total charging (blank = typical) | PSS/E + PSCAD
Plant | Gen-tie C per length | tie_c_per | uF |  |  | instead of B | PSS/E + PSCAD
Plant | Gen-tie R total | tie_r_ohm | ohm |  |  | instead of per length (one circuit) | PSS/E + PSCAD
Plant | Gen-tie X total | tie_x_ohm | ohm |  |  |  | PSS/E + PSCAD
Plant | Gen-tie B total | tie_b_us | uS |  |  |  | PSS/E + PSCAD
Plant | Gen-tie circuits | tie_parallel |  | 1 |  | identical circuits in parallel (blank = 1) | PSS/E + PSCAD
Plant | Gen-tie rating | tie_rate_mva | MVA | typical for the POI kV |  | one circuit (blank = typical for the POI kV) | PSS/E + PSCAD
Plant | Control mode | control_mode |  |  | Q ¦ PF ¦ V | Q: Q at the POI ¦ PF: power factor at the POI ¦ V: the plant holds the POI voltage with the grid at Grid voltage | PSS/E + PSCAD
Plant | POI voltage | v_poi_pu | pu | 1.0 |  | the POI voltage the plant holds (blank = 1.0) | PSS/E + PSCAD
Plant | Q at POI | q_poi_mvar | MVAr | 0 |  | mode Q; + = into the grid (blank = 0) | PSS/E + PSCAD
Plant | PF at POI | pf_poi |  |  |  | mode PF; + lagging (Q into the grid), - leading | PSS/E + PSCAD
Plant | Grid voltage | v_grid_pu | pu | 1.0 |  | mode V: the infinite bus (blank = 1.0) | PSS/E + PSCAD
Plant | P at POI | p_poi_mw | MW | each generator at its dispatch |  | blank = each generator at its dispatch ¦ a value = the dispatches scaled to deliver it | PSS/E + PSCAD
Plant | Plant controller | plant_ctrl |  | REPC_A | REPC_A ¦ REPC_B | PSS/E .dyr -- REPC_A: a REPCA1 on each generator ¦ REPC_B: one for the plant, PLNTBU1 at the POI and a REAX4BU1 on each generator (hybrid plants) (blank = REPC_A) | PSS/E .dyr
Plant | REGC_A / REPC_A records | regc_repc |  | standard | standard ¦ USRMDL | standard: REGCA1 / REPCA1 (PSS/E library) ¦ USRMDL: REGCAU1 / REPCAU1 (the WECC user-model DLL) (blank = standard) | PSS/E .dyr
Plant | PSCAD time step | pscad_time_step_us | us | 10 (the vendor model's own requirement wins |  | blank = 10 (the vendor model's own requirement wins) | PSCAD
Plant | PSCAD duration | pscad_duration_s | s | 5 |  | blank = 5 | PSCAD
Plant | PSCAD plot step | pscad_plot_step_us | us | 100 |  | blank = 100 | PSCAD
Plant | PSCAD meter at POI | pscad_meter |  |  | YES ¦ NO | YES = a multimeter between the grid and the POI | PSCAD
Plant | PSCAD lines as | pscad_lines |  | PI | PI ¦ RLC | PI = the gen-tie, each collector and each feeder section one Coupled PI Section (R, X, B in pu, its charging inside); RLC = an R and an L, the charging a C at each end (blank = PI) | PSCAD
Plant | PSCAD fault at POI | pscad_fault |  |  | YES ¦ NO | YES = a fault on the grid side of the POI with its timed fault logic, as vendors' test cases have | PSCAD
Plant | PSCAD fault time | pscad_fault_s | s | 100: none in the run |  | when the fault starts (blank = 100: none in the run) | PSCAD
Plant | PSCAD fault duration | pscad_fault_dur_s | s | 0.15 |  | blank = 0.15 | PSCAD
Plant | PSCAD fault type | pscad_fault_type |  | ABCG | ABCG ¦ ABC ¦ AG ¦ BG ¦ CG ¦ ABG ¦ BCG ¦ ACG ¦ AB ¦ BC ¦ AC | the phases faulted, G = to ground (blank = ABCG) | PSCAD
Plant | PSCAD fault resistance | pscad_fault_ohm | ohm | 0.01 |  | blank = 0.01 | PSCAD
Plant | PSCAD libraries | pscad_libraries |  |  |  | user-model libraries (.pslx) to load, separated by ; | PSCAD
MPT
MPT | Name | name |  |  |  | MPT name. Its buses: <name> or <name>:LV (LV winding), <name>:TV (tertiary) | PSS/E + PSCAD
MPT | HV kV | hv_kv |  |  |  |  | PSS/E + PSCAD
MPT | LV kV | lv_kv |  |  |  |  | PSS/E + PSCAD
MPT | TV kV | tv_kv |  | two windings |  | tertiary / 2nd LV winding; blank = two windings | PSS/E + PSCAD
MPT | MVA | mva |  |  |  | the rating (3 windings: HV winding) | PSS/E + PSCAD
MPT | LV MVA | lv_mva |  |  |  | 3 windings | PSS/E + PSCAD
MPT | TV MVA | tv_mva |  |  |  | 3 windings | PSS/E + PSCAD
MPT | Z HV-LV % | z_hl_pct |  |  |  | on its base MVA | PSS/E + PSCAD
MPT | Z HV-TV % | z_ht_pct |  |  |  | 3 windings | PSS/E + PSCAD
MPT | Z LV-TV % | z_lt_pct |  |  |  | 3 windings | PSS/E + PSCAD
MPT | Z HV-LV base MVA | base_hl_mva |  | MVA |  | blank = MVA | PSS/E + PSCAD
MPT | Z HV-TV base MVA | base_ht_mva |  | MVA |  | blank = MVA | PSS/E + PSCAD
MPT | Z LV-TV base MVA | base_lt_mva |  | MVA |  | blank = MVA | PSS/E + PSCAD
MPT | X/R | x_r |  |  |  | each impedance | PSS/E + PSCAD
MPT | Load loss kW | load_loss_kw |  |  |  | 2 windings, at MVA: instead of X/R | PSS/E + PSCAD
MPT | Vector group | vector |  |  |  | YNd1, YNd11, Dyn1, YNyn0, YNd1d1 ... | PSS/E + PSCAD
MPT | HV tap | tap |  | 1 |  | HV winding ratio, 1.025 = +2.5 % (blank = 1) | PSS/E + PSCAD
MPT | Parallel units | count |  | 1 |  | identical units (blank = 1) | PSS/E + PSCAD
MPT | No-load loss % | nll_pct |  | 0 |  | of MVA (blank = 0) | PSS/E + PSCAD
MPT | Magnetising current % | im_pct |  | 0 |  | of MVA (blank = 0) | PSS/E + PSCAD
MPT | Rating MVA | rate_mva |  | MVA |  | blank = MVA | PSS/E + PSCAD
MPT | Tie length | tie_length |  | none |  | a line of its own from HV to this MPT (blank = none) | PSS/E + PSCAD
MPT | Tie length unit | tie_unit |  |  | km ¦ mi ¦ kft ¦ m ¦ ft |  | PSS/E + PSCAD
MPT | Tie values per | tie_per_unit |  | Tie length unit | km ¦ mi ¦ kft ¦ m ¦ ft | the length R, X, B are per (blank = Tie length unit) | PSS/E + PSCAD
MPT | Tie R per length | tie_r_per |  | a typical overhead line of the HV kV |  | ohm (blank = a typical overhead line of the HV kV) | PSS/E + PSCAD
MPT | Tie X per length | tie_x_per |  | typical |  | ohm (blank = typical) | PSS/E + PSCAD
MPT | Tie B per length | tie_b_per |  | typical |  | uS (blank = typical) | PSS/E + PSCAD
MPT | Tie rating MVA | tie_rate_mva |  | typical |  | blank = typical | PSS/E + PSCAD
Generators
Generators | Name | name |  |  |  | generator name. Its buses: <name>:MV (GSU HV), <name> or <name>:LV (terminal) | PSS/E + PSCAD
Generators | Type | type |  |  | PV ¦ BESS ¦ WT4 ¦ WT3 ¦ SYNC ¦ USER | PV BESS WT4 WT3 SYNC USER (USER: Dyr_Records only) | PSS/E + PSCAD
Generators | Machine ID | id |  | 1 |  | blank = 1 | PSS/E + PSCAD
Generators | Connect to | connect |  |  |  | the bus its collector starts from: MPT1 (LV), MPT1:TV, a shared collector, HV, POI | PSS/E + PSCAD
Generators | Units | units |  |  |  | number of units | PSS/E + PSCAD
Generators | Unit MVA | unit_mva |  | from P and Q |  | one unit (blank = from P and Q) | PSS/E + PSCAD
Generators | Unit Pmax MW | unit_pmax_mw |  |  |  |  | PSS/E + PSCAD
Generators | Unit Pmin MW | unit_pmin_mw |  | 0 |  | BESS charging: negative (blank = 0) | PSS/E + PSCAD
Generators | Unit Qmax MVAr | unit_qmax_mvar |  | from Unit PF |  | blank = from Unit PF | PSS/E + PSCAD
Generators | Unit Qmin MVAr | unit_qmin_mvar |  | -Qmax |  | blank = -Qmax | PSS/E + PSCAD
Generators | Unit PF | unit_pf |  | 0.95 |  | Q at Pmax when Qmax is blank (blank = 0.95) | PSS/E + PSCAD
Generators | Terminal kV | kv |  | GSU LV kV |  | blank = GSU LV kV | PSS/E + PSCAD
Generators | Dispatch MW | dispatch_mw |  | Pmax (BESS charging: negative |  | this generator's total; blank = Pmax (BESS charging: negative) | PSS/E + PSCAD
Generators | Q mode | q_mode |  |  | share ¦ fixed | share: holds the POI with the other share generators ¦ fixed: its own Q | PSS/E + PSCAD
Generators | Fixed Q MVAr | fixed_q_mvar |  | 0 |  | Q mode fixed (blank = 0) | PSS/E + PSCAD
Generators | Fixed PF | fixed_pf |  |  |  | Q mode fixed, instead of Fixed Q (+ lagging) | PSS/E + PSCAD
Generators | GSU count | gsu_count |  | Units |  | blank = Units | PSS/E + PSCAD
Generators | GSU MVA | gsu_mva |  | no GSU (units on the MV bus |  | one GSU; blank = no GSU (units on the MV bus) | PSS/E + PSCAD
Generators | GSU HV kV | gsu_hv_kv |  |  |  |  | PSS/E + PSCAD
Generators | GSU LV kV | gsu_lv_kv |  |  |  |  | PSS/E + PSCAD
Generators | GSU Z % | gsu_z_pct |  |  |  | on GSU MVA | PSS/E + PSCAD
Generators | GSU X/R | gsu_x_r |  |  |  |  | PSS/E + PSCAD
Generators | GSU vector group | gsu_vector |  |  |  |  | PSS/E + PSCAD
Generators | GSU HV tap | gsu_tap |  | 1 |  | blank = 1 | PSS/E + PSCAD
Generators | Collector | collector |  |  | FEEDERS ¦ EQUIVALENT ¦ NONE | FEEDERS: WECC equivalent of its Feeders rows ¦ EQUIVALENT: R X B here ¦ NONE | PSS/E + PSCAD
Generators | Collector R | coll_r |  |  |  | EQUIVALENT | PSS/E + PSCAD
Generators | Collector X | coll_x |  |  |  | EQUIVALENT | PSS/E + PSCAD
Generators | Collector B | coll_b |  |  |  | EQUIVALENT, total charging | PSS/E + PSCAD
Generators | Collector units | coll_units |  |  | pu ¦ ohm | pu: system base at collector kV ¦ ohm: R X in ohm, B in uS | PSS/E + PSCAD
Generators | ZSORCE X pu | zsorce_x |  |  |  | on MBASE (blank: inverters 9999, SYNC X''d) | PSS/E .dyr
Generators | WMOD | wmod |  |  |  | blank: inverters 1, SYNC 0 | PSS/E .dyr
Generators | Electrical control | reec |  | REEC_A, BESS REEC_C | REEC_A ¦ REEC_C ¦ REEC_D | PSS/E .dyr -- REEC_A: PV, WT ¦ REEC_C: BESS ¦ REEC_D: PV, BESS, WT4 (blank = REEC_A, BESS REEC_C) | PSS/E .dyr
Generators | PSCAD library | pscad_library |  | none |  | vendor library .pslx (blank = none) | PSCAD
Generators | PSCAD definition | pscad_definition |  | a source: network check |  | vendor model, library:name (blank = a source: network check) | PSCAD
Generators | PSCAD AC port | pscad_ac_port |  | its 3-phase port |  | its AC port (blank = its 3-phase port) | PSCAD
Generators | PSCAD source case | pscad_source |  |  |  | the OEM's PSCAD model (.pscx / .pslx) the UDM comes from: its PSCAD definition added to the case (GUI: Pick UDM from OEM model) | PSCAD
Generators | PSCAD component ID | pscad_component_id |  | the definition, its values from PSCAD_Params |  | a UDM placed in the source case: copied with its settings instead (blank = the definition, its values from PSCAD_Params) | PSCAD
Generators | PSCAD inverter at | pscad_inv_at |  | LV | LV ¦ MV | LV: the inverter (your UDM or the stand-in source) on the GSU's LV side, the GSU built ¦ MV: on its HV side, for a UDM with its GSU inside (blank = LV) | PSCAD
Feeders
Feeders | Collector | collector |  |  |  | the generator (its own collector) or a shared collector | PSS/E + PSCAD
Feeders | Feeder | feeder |  |  |  | feeder name | PSS/E + PSCAD
Feeders | Copies | copies |  | 1 |  | identical feeders (blank = 1) | PSS/E + PSCAD
Feeders | Section | section |  |  |  | 1, 2, 3 ... from the collector bus out | PSS/E + PSCAD
Feeders | From section | from_section |  | the one before (daisy chain |  | blank = the one before (daisy chain) ¦ 0 = the collector bus ¦ n = a lateral off the end of section n | PSS/E + PSCAD
Feeders | Cable | cable |  |  |  | from Cables | PSS/E + PSCAD
Feeders | Length | length |  |  |  |  | PSS/E + PSCAD
Feeders | Length unit | unit |  | km | km ¦ mi ¦ kft ¦ m ¦ ft | blank = km | PSS/E + PSCAD
Feeders | Units at end | units |  |  |  | units tapped at the far end | PSS/E + PSCAD
Feeders | Units of | units_of |  |  |  | shared collectors: whose units (repeat the section for another generator's) | PSS/E + PSCAD
Feeders | Parallel cables | parallel |  | 1 |  | blank = 1 | PSS/E + PSCAD
Feeders | R ohm | r_ohm |  | Cable x Length |  | the section's R, its parallel cables together (blank = Cable x Length) | PSS/E + PSCAD
Feeders | X ohm | x_ohm |  | Cable x Length |  | the section's X (blank = Cable x Length) | PSS/E + PSCAD
Feeders | B uS | b_us |  | Cable x Length |  | the section's charging B, total (blank = Cable x Length) | PSS/E + PSCAD
Cables
Cables | Cable | cable |  |  |  | cable type | PSS/E + PSCAD
Cables | Length unit | unit |  |  | km ¦ mi ¦ kft ¦ m ¦ ft | the values are per | PSS/E + PSCAD
Cables | R per length | r_per |  |  |  | ohm, at operating temperature | PSS/E + PSCAD
Cables | X per length | x_per |  |  |  | ohm | PSS/E + PSCAD
Cables | C per length | c_per |  |  |  | uF | PSS/E + PSCAD
Cables | B per length | b_per |  |  |  | uS, instead of C | PSS/E + PSCAD
Collectors
Collectors | Name | name |  |  |  | shared collector: its far-end bus has this name | PSS/E + PSCAD
Collectors | Connect to | connect |  |  |  | the bus it starts from (MPT1, MPT1:TV ...) | PSS/E + PSCAD
Loads_Shunts
Loads_Shunts | Kind | kind |  |  | LOAD ¦ SHUNT | LOAD: constant impedance ¦ SHUNT: + capacitor, - reactor | PSS/E + PSCAD
Loads_Shunts | At bus | at |  |  |  | POI, HV, MPT1, MPT1:TV, PV:MV, PV ... | PSS/E + PSCAD
Loads_Shunts | MW | mw |  |  |  | LOAD, at 1 pu | PSS/E + PSCAD
Loads_Shunts | MVAr | mvar |  |  |  | at 1 pu: LOAD + inductive ¦ SHUNT + capacitive | PSS/E + PSCAD
Loads_Shunts | Name | name |  |  |  |  | PSS/E + PSCAD
Machines
Machines | Machine | machine |  |  |  | DETAILED model: a machine, <generator>_<feeder>_S<section> (the GUI lists them); its values in place of its share of its generator's | PSS/E + PSCAD
Machines | Machine ID | id |  | its generator's |  | blank = its generator's | PSS/E + PSCAD
Machines | Pgen MW | pgen_mw |  | its share of its generator's Dispatch MW |  | its dispatch (blank = its share of its generator's Dispatch MW) | PSS/E + PSCAD
Machines | Pmax MW | pmax_mw |  | its units x Unit Pmax |  | blank = its units x Unit Pmax | PSS/E + PSCAD
Machines | Pmin MW | pmin_mw |  | its units x Unit Pmin |  | blank = its units x Unit Pmin | PSS/E + PSCAD
Machines | Qmax MVAr | qmax_mvar |  | its units x Unit Qmax |  | blank = its units x Unit Qmax | PSS/E + PSCAD
Machines | Qmin MVAr | qmin_mvar |  | its units x Unit Qmin |  | blank = its units x Unit Qmin | PSS/E + PSCAD
Machines | Fixed Q MVAr | q_mvar |  | as its generator's Q mode |  | a value: this Q, fixed (blank = as its generator's Q mode) | PSS/E + PSCAD
Machines | MBASE MVA | mbase_mva |  | its units x Unit MVA |  | blank = its units x Unit MVA | PSS/E + PSCAD
Bus_Numbers
Bus_Numbers | Bus | bus |  |  |  | its role: IB, POI, HV, MPT1:LV, PV:MV, PV:LV ... | PSS/E + PSCAD
Bus_Numbers | Number | number |  | automatic |  | blank = automatic | PSS/E + PSCAD
Bus_Numbers | Name | name |  | automatic (12 characters at most |  | blank = automatic (12 characters at most) | PSS/E + PSCAD
Dyr_Params
Dyr_Params | Generator | generator |  |  |  | IB: the infinite bus ¦ PLANT: the plant controller (REPC_B) | PSS/E .dyr
Dyr_Params | Model | model |  |  |  | REGCA1 (REGCAU1) ¦ REECA1 REECCU1 REECDU1 ¦ REPCA1 (REPCAU1) or REAX4BU1 ¦ PLANT: PLNTBU1 ¦ WT3: + WTDTA1 WTARA1 WTPTA1 WTTQA1 ¦ SYNC: GENROU SEXS TGOV1 ¦ IB: GENCLS | PSS/E .dyr
Dyr_Params | Parameter | parameter |  |  |  | PSS/E name (the report lists them all) or position: ICON2, CON14 | PSS/E .dyr
Dyr_Params | Value | value |  |  |  |  | PSS/E .dyr
Dyr_Records
Dyr_Records | Generator | generator |  | the plant |  | blank = the plant | PSS/E .dyr
Dyr_Records | Record | record |  |  |  | .dyr text ending in / -- {BUS} {ID} {MBASE} {POI} {IB} {HV} {MV} {<bus role>} are filled in | PSS/E .dyr
PSCAD_Params
PSCAD_Params | Generator | generator |  |  |  |  | PSCAD
PSCAD_Params | Parameter | parameter |  |  |  | the vendor model's parameter name | PSCAD
PSCAD_Params | Value | value |  |  |  | as PSCAD takes it (0.63 [kV], 40, {UNITS}, {P_PU} ...) | PSCAD
BUS NAMES -- Connect to, At, Bus_Numbers and {<bus>} in Dyr_Records take these
| IB |  |  |  |  | the infinite bus
| POI |  |  |  |  | the point of interconnection
| HV |  |  |  |  | the gen-tie's plant end (the POI when there is no gen-tie)
| <MPT> or <MPT>:LV |  |  |  |  | an MPT's LV winding
| <MPT>:TV |  |  |  |  | a 3-winding MPT's tertiary
| <MPT>:HV |  |  |  |  | an MPT with a tie line of its own: its HV end
| <collector> |  |  |  |  | a shared collector's far end
| <generator>:MV |  |  |  |  | a generator's GSU HV side
| <generator> or <generator>:LV |  |  |  |  | a generator's terminal
| <collector>_<feeder>_S<n> |  |  |  |  | DETAILED: the far end of feeder section n
| <generator>_<feeder>_S<n>:LV |  |  |  |  | DETAILED: the terminal of the units at that node
PSCAD_Params PLACEHOLDERS -- filled in for each inverter a vendor model stands for
PSCAD_Params | {UNITS} |  |  |  |  | the units the inverter stands for | PSCAD
PSCAD_Params | {MVA} |  |  |  |  | their MVA | PSCAD
PSCAD_Params | {P_MW} |  |  |  |  | their P where the inverter connects (MW) | PSCAD
PSCAD_Params | {Q_MVAR} |  |  |  |  | their Q there (MVAr) | PSCAD
PSCAD_Params | {P_PU} |  |  |  |  | P on {MVA} | PSCAD
PSCAD_Params | {Q_PU} |  |  |  |  | Q on {MVA} | PSCAD
PSCAD_Params | {UNIT_MVA} |  |  |  |  | one unit's MVA | PSCAD
PSCAD_Params | {UNIT_P_MW} |  |  |  |  | one unit's P (MW) | PSCAD
PSCAD_Params | {UNIT_Q_MVAR} |  |  |  |  | one unit's Q (MVAr) | PSCAD
PSCAD_Params | {V_PU} |  |  |  |  | the voltage where it connects (pu) | PSCAD
PSCAD_Params | {V_KV} |  |  |  |  | the same in kV | PSCAD
PSCAD_Params | {KV} |  |  |  |  | that bus's base kV | PSCAD
PSCAD_Params | {ANGLE} |  |  |  |  | its PSCAD angle (deg, the transformers' phase shifts included) | PSCAD
PSCAD_Params | {FREQ} |  |  |  |  | frequency (Hz) | PSCAD
PSCAD_Params | {P_INV_MW} |  |  |  |  | P at the inverters' own terminals (MW; a UDM on the MV side) | PSCAD
PSCAD_Params | {Q_INV_MVAR} |  |  |  |  | Q there (MVAr) | PSCAD
PSCAD_Params | {V_INV_PU} |  |  |  |  | the voltage there (pu) | PSCAD

## Dynamic_Models
DYNAMIC MODELS ¦ every parameter, its default and meaning
To change one: a row in Dyr_Params with the Generator (IB: the infinite bus, PLANT: the plant controller), the Model, the Parameter (or its position) and the Value. 'auto' values come from the plant data (limits on MBASE, buses, shares).
Model | Position | Parameter | Default | Set by the script | Description
GENCLS -- infinite bus (IB): classical machine, H = 0
GENCLS | CON1 | H | 0 |  | inertia constant (s; 0 = infinite bus)
GENCLS | CON2 | D | 0 |  | damping (pu)
REGCA1 -- generator / converter interface, inverters (REGC_A)
REGCA1 | ICON1 | LVPLSW | 1 |  | low-voltage power logic: 0 off, 1 on
REGCA1 | CON1 | Tg | 0.02 |  | converter current control time constant (s)
REGCA1 | CON2 | Rrpwr | 10 |  | active current recovery rate after a fault (pu/s)
REGCA1 | CON3 | Brkpt | 0.9 |  | LVPL breakpoint voltage (pu)
REGCA1 | CON4 | Zerox | 0.4 |  | LVPL zero-crossing voltage (pu)
REGCA1 | CON5 | Lvpl1 | 1.22 |  | LVPL current limit at the breakpoint (pu)
REGCA1 | CON6 | Volim | 1.2 |  | high-voltage reactive current limit: voltage (pu)
REGCA1 | CON7 | Lvpnt1 | 0.8 |  | low-voltage active current management: upper voltage (pu)
REGCA1 | CON8 | Lvpnt0 | 0.4 |  | low-voltage active current management: lower voltage (pu)
REGCA1 | CON9 | Iolim | -1.3 |  | high-voltage clamp: current limit (pu, negative)
REGCA1 | CON10 | Tfltr | 0.02 |  | voltage (or Q) measurement filter time constant (s)
REGCA1 | CON11 | Khv | 0.7 |  | high-voltage clamp acceleration factor
REGCA1 | CON12 | Iqrmax | 99 |  | reactive current rate up (pu/s)
REGCA1 | CON13 | Iqrmin | -99 |  | reactive current rate down (pu/s)
REGCA1 | CON14 | Accel | 0.7 |  | acceleration factor of the converter's network solution
REECA1 -- electrical control REEC_A: PV, wind (WT3, WT4)
REECA1 | ICON1 | BUSR | 0 |  | regulated bus (0 = the terminal)
REECA1 | ICON2 | PFFLAG | 0 |  | 1 constant power factor, 0 Q control
REECA1 | ICON3 | VFLAG | 0 |  | 1 voltage loop (Kvp, Kvi) after the Q loop, 0 Q loop only
REECA1 | ICON4 | QFLAG | 0 |  | 1 voltage / Q control, 0 constant power factor or Q
REECA1 | ICON5 | PFLAG | 0 | auto | 1 P reference times speed (wind)
REECA1 | ICON6 | PQFLAG | 0 |  | at the current limit: 0 Q priority, 1 P priority
REECA1 | CON1 | Vdip | 0.9 |  | voltage below which the dip logic acts (pu)
REECA1 | CON2 | Vup | 1.1 |  | voltage above which the dip logic acts (pu)
REECA1 | CON3 | Trv | 0.02 |  | terminal voltage filter time constant (s)
REECA1 | CON4 | dbd1 | -0.05 |  | deadband, lower edge (pu, 0 or less)
REECA1 | CON5 | dbd2 | 0.05 |  | deadband, upper edge (pu, 0 or more)
REECA1 | CON6 | Kqv | 2 |  | reactive current injection gain in a dip (pu/pu)
REECA1 | CON7 | Iqh1 | 1.05 |  | reactive current injection, upper limit (pu)
REECA1 | CON8 | Iql1 | -1.05 |  | reactive current injection, lower limit (pu)
REECA1 | CON9 | Vref0 | 0 |  | reference voltage for the injection (pu; 0 = the initial terminal voltage)
REECA1 | CON10 | Iqfrz | 0 |  | reactive current held after a dip (pu)
REECA1 | CON11 | Thld | 0 |  | time the injection is held after a dip (s)
REECA1 | CON12 | Thld2 | 0 |  | time the active current limit is held after a dip (s)
REECA1 | CON13 | Tp | 0.02 |  | active power measurement filter time constant (s)
REECA1 | CON14 | QMax | 0.4 | auto | Q limit, upper (pu on MBASE)
REECA1 | CON15 | QMin | -0.4 | auto | Q limit, lower (pu on MBASE)
REECA1 | CON16 | VMAX | 1.1 |  | voltage control limit, upper (pu)
REECA1 | CON17 | VMIN | 0.9 |  | voltage control limit, lower (pu)
REECA1 | CON18 | Kqp | 0 |  | Q loop proportional gain
REECA1 | CON19 | Kqi | 0.1 |  | Q loop integral gain
REECA1 | CON20 | Kvp | 0 |  | voltage loop proportional gain
REECA1 | CON21 | Kvi | 40 |  | voltage loop integral gain
REECA1 | CON22 | Vref1 | 0 |  | voltage reference with VFLAG 0 (pu)
REECA1 | CON23 | Tiq | 0.02 |  | reactive current command time constant (s)
REECA1 | CON24 | dPmax | 99 |  | P reference ramp up (pu/s)
REECA1 | CON25 | dPmin | -99 |  | P reference ramp down (pu/s)
REECA1 | CON26 | PMAX | 1 | auto | P limit, upper (pu on MBASE)
REECA1 | CON27 | PMIN | 0 | auto | P limit, lower (pu on MBASE; negative: charging)
REECA1 | CON28 | Imax | 1.1 |  | converter current limit (pu on MBASE)
REECA1 | CON29 | Tpord | 0.02 |  | P order filter time constant (s)
REECA1 | CON30 | Vq1 | 0.2 |  | reactive current limit curve (VDL1), point 1: voltage (pu)
REECA1 | CON31 | Iq1 | 1.1 |  | reactive current limit curve (VDL1), point 1: current limit (pu)
REECA1 | CON32 | Vq2 | 0.5 |  | reactive current limit curve (VDL1), point 2: voltage (pu)
REECA1 | CON33 | Iq2 | 1.1 |  | reactive current limit curve (VDL1), point 2: current limit (pu)
REECA1 | CON34 | Vq3 | 0.8 |  | reactive current limit curve (VDL1), point 3: voltage (pu)
REECA1 | CON35 | Iq3 | 1.1 |  | reactive current limit curve (VDL1), point 3: current limit (pu)
REECA1 | CON36 | Vq4 | 1.2 |  | reactive current limit curve (VDL1), point 4: voltage (pu)
REECA1 | CON37 | Iq4 | 1.1 |  | reactive current limit curve (VDL1), point 4: current limit (pu)
REECA1 | CON38 | Vp1 | 0.2 |  | active current limit curve (VDL2), point 1: voltage (pu)
REECA1 | CON39 | Ip1 | 1.1 |  | active current limit curve (VDL2), point 1: current limit (pu)
REECA1 | CON40 | Vp2 | 0.5 |  | active current limit curve (VDL2), point 2: voltage (pu)
REECA1 | CON41 | Ip2 | 1.1 |  | active current limit curve (VDL2), point 2: current limit (pu)
REECA1 | CON42 | Vp3 | 0.8 |  | active current limit curve (VDL2), point 3: voltage (pu)
REECA1 | CON43 | Ip3 | 1.1 |  | active current limit curve (VDL2), point 3: current limit (pu)
REECA1 | CON44 | Vp4 | 1.2 |  | active current limit curve (VDL2), point 4: voltage (pu)
REECA1 | CON45 | Ip4 | 1.1 |  | active current limit curve (VDL2), point 4: current limit (pu)
REPCA1 -- plant controller REPC_A, one on each generator (Plant controller REPC_A)
REPCA1 | ICON1 | BUSR |  | auto | regulated bus (0 = the terminal)
REPCA1 | ICON2 | BUS1 |  | auto | P and Q measured on the branch from this bus
REPCA1 | ICON3 | BUS2 |  | auto | ... to this bus
REPCA1 | ICON4 | CKT |  | auto | ... this circuit
REPCA1 | ICON5 | VCFLAG | 1 |  | 1 voltage control with line drop compensation, 0 reactive droop
REPCA1 | ICON6 | REFFLAG | 1 |  | 1 voltage control, 0 Q control
REPCA1 | ICON7 | FFLAG | 1 |  | 1 frequency response on, 0 off
REPCA1 | CON1 | Tfltr | 0.02 |  | voltage (or Q) measurement filter time constant (s)
REPCA1 | CON2 | Kp | 1 |  | voltage / Q loop proportional gain
REPCA1 | CON3 | Ki | 5 |  | voltage / Q loop integral gain
REPCA1 | CON4 | Tft | 0 |  | lead time constant (s)
REPCA1 | CON5 | Tfv | 0.075 |  | lag time constant (s)
REPCA1 | CON6 | Vfrz | 0.7 |  | voltage below which the controller freezes (pu)
REPCA1 | CON7 | Rc | 0 |  | current / line drop compensation resistance (pu)
REPCA1 | CON8 | Xc | 0 |  | current / line drop compensation reactance (pu)
REPCA1 | CON9 | Kc | 0 |  | reactive droop gain
REPCA1 | CON10 | emax | 0.1 |  | error limit, upper (pu)
REPCA1 | CON11 | emin | -0.1 |  | error limit, lower (pu)
REPCA1 | CON12 | dbd1 | 0 |  | deadband, lower edge (pu, 0 or less)
REPCA1 | CON13 | dbd2 | 0 |  | deadband, upper edge (pu, 0 or more)
REPCA1 | CON14 | Qmax | 0.4 | auto | Q command limit, upper (pu)
REPCA1 | CON15 | Qmin | -0.4 | auto | Q command limit, lower (pu)
REPCA1 | CON16 | Kpg | 0.1 |  | frequency (P) loop proportional gain
REPCA1 | CON17 | Kig | 0.05 |  | frequency (P) loop integral gain
REPCA1 | CON18 | Tp | 0.25 |  | active power measurement filter time constant (s)
REPCA1 | CON19 | fdbd1 | -0.0006 |  | frequency deadband, lower edge (pu)
REPCA1 | CON20 | fdbd2 | 0.0006 |  | frequency deadband, upper edge (pu)
REPCA1 | CON21 | femax | 999 |  | frequency error limit, upper (pu)
REPCA1 | CON22 | femin | -999 |  | frequency error limit, lower (pu)
REPCA1 | CON23 | Pmax | 1 | auto | P command limit, upper (pu)
REPCA1 | CON24 | Pmin | 0 | auto | P command limit, lower (pu)
REPCA1 | CON25 | Tlag | 0.1 |  | P command lag time constant (s)
REPCA1 | CON26 | Ddn | 20 |  | droop gain, over-frequency (pu P / pu f)
REPCA1 | CON27 | Dup | 0 | auto | droop gain, under-frequency (pu P / pu f)
REGCAU1 -- REGC_A as the WECC user model (Plant: REGC_A / REPC_A records USRMDL)
REGCAU1 | ICON1 | LVPLSW | 1 |  | low-voltage power logic: 0 off, 1 on
REGCAU1 | CON1 | Tg | 0.02 |  | converter current control time constant (s)
REGCAU1 | CON2 | Rrpwr | 10 |  | active current recovery rate after a fault (pu/s)
REGCAU1 | CON3 | Brkpt | 0.9 |  | LVPL breakpoint voltage (pu)
REGCAU1 | CON4 | Zerox | 0.4 |  | LVPL zero-crossing voltage (pu)
REGCAU1 | CON5 | Lvpl1 | 1.22 |  | LVPL current limit at the breakpoint (pu)
REGCAU1 | CON6 | Volim | 1.2 |  | high-voltage reactive current limit: voltage (pu)
REGCAU1 | CON7 | Lvpnt1 | 0.8 |  | low-voltage active current management: upper voltage (pu)
REGCAU1 | CON8 | Lvpnt0 | 0.4 |  | low-voltage active current management: lower voltage (pu)
REGCAU1 | CON9 | Iolim | -1.3 |  | high-voltage clamp: current limit (pu, negative)
REGCAU1 | CON10 | Tfltr | 0.02 |  | voltage (or Q) measurement filter time constant (s)
REGCAU1 | CON11 | Khv | 0.7 |  | high-voltage clamp acceleration factor
REGCAU1 | CON12 | Iqrmax | 99 |  | reactive current rate up (pu/s)
REGCAU1 | CON13 | Iqrmin | -99 |  | reactive current rate down (pu/s)
REGCAU1 | CON14 | Accel | 0.7 |  | acceleration factor of the converter's network solution
REECCU1 -- electrical control REEC_C: BESS, with state of charge
REECCU1 | ICON1 | BUSR | 0 |  | regulated bus (0 = the terminal)
REECCU1 | ICON2 | PFFLAG | 0 |  | 1 constant power factor, 0 Q control
REECCU1 | ICON3 | VFLAG | 0 |  | 1 voltage loop (Kvp, Kvi) after the Q loop, 0 Q loop only
REECCU1 | ICON4 | QFLAG | 0 |  | 1 voltage / Q control, 0 constant power factor or Q
REECCU1 | ICON5 | PQFLAG | 0 |  | at the current limit: 0 Q priority, 1 P priority
REECCU1 | CON1 | Vdip | 0.9 |  | voltage below which the dip logic acts (pu)
REECCU1 | CON2 | Vup | 1.1 |  | voltage above which the dip logic acts (pu)
REECCU1 | CON3 | Trv | 0.02 |  | terminal voltage filter time constant (s)
REECCU1 | CON4 | dbd1 | -0.05 |  | deadband, lower edge (pu, 0 or less)
REECCU1 | CON5 | dbd2 | 0.05 |  | deadband, upper edge (pu, 0 or more)
REECCU1 | CON6 | Kqv | 2 |  | reactive current injection gain in a dip (pu/pu)
REECCU1 | CON7 | Iqh1 | 1.05 |  | reactive current injection, upper limit (pu)
REECCU1 | CON8 | Iql1 | -1.05 |  | reactive current injection, lower limit (pu)
REECCU1 | CON9 | Vref0 | 0 |  | reference voltage for the injection (pu; 0 = the initial terminal voltage)
REECCU1 | CON10 | Tp | 0.02 |  | active power measurement filter time constant (s)
REECCU1 | CON11 | QMax | 0.4 | auto | Q limit, upper (pu on MBASE)
REECCU1 | CON12 | QMin | -0.4 | auto | Q limit, lower (pu on MBASE)
REECCU1 | CON13 | VMAX | 1.1 |  | voltage control limit, upper (pu)
REECCU1 | CON14 | VMIN | 0.9 |  | voltage control limit, lower (pu)
REECCU1 | CON15 | Kqp | 0 |  | Q loop proportional gain
REECCU1 | CON16 | Kqi | 0.1 |  | Q loop integral gain
REECCU1 | CON17 | Kvp | 0 |  | voltage loop proportional gain
REECCU1 | CON18 | Kvi | 40 |  | voltage loop integral gain
REECCU1 | CON19 | Tiq | 0.02 |  | reactive current command time constant (s)
REECCU1 | CON20 | dPmax | 99 |  | P reference ramp up (pu/s)
REECCU1 | CON21 | dPmin | -99 |  | P reference ramp down (pu/s)
REECCU1 | CON22 | PMAX | 1 | auto | P limit, upper (pu on MBASE)
REECCU1 | CON23 | PMIN | -1 | auto | P limit, lower (pu on MBASE; negative: charging)
REECCU1 | CON24 | Imax | 1.1 |  | converter current limit (pu on MBASE)
REECCU1 | CON25 | Tpord | 0.02 |  | P order filter time constant (s)
REECCU1 | CON26 | Vq1 | 0.2 |  | reactive current limit curve (VDL1), point 1: voltage (pu)
REECCU1 | CON27 | Iq1 | 1.1 |  | reactive current limit curve (VDL1), point 1: current limit (pu)
REECCU1 | CON28 | Vq2 | 0.5 |  | reactive current limit curve (VDL1), point 2: voltage (pu)
REECCU1 | CON29 | Iq2 | 1.1 |  | reactive current limit curve (VDL1), point 2: current limit (pu)
REECCU1 | CON30 | Vq3 | 0.8 |  | reactive current limit curve (VDL1), point 3: voltage (pu)
REECCU1 | CON31 | Iq3 | 1.1 |  | reactive current limit curve (VDL1), point 3: current limit (pu)
REECCU1 | CON32 | Vq4 | 1.2 |  | reactive current limit curve (VDL1), point 4: voltage (pu)
REECCU1 | CON33 | Iq4 | 1.1 |  | reactive current limit curve (VDL1), point 4: current limit (pu)
REECCU1 | CON34 | Vp1 | 0.2 |  | active current limit curve (VDL2), point 1: voltage (pu)
REECCU1 | CON35 | Ip1 | 1.1 |  | active current limit curve (VDL2), point 1: current limit (pu)
REECCU1 | CON36 | Vp2 | 0.5 |  | active current limit curve (VDL2), point 2: voltage (pu)
REECCU1 | CON37 | Ip2 | 1.1 |  | active current limit curve (VDL2), point 2: current limit (pu)
REECCU1 | CON38 | Vp3 | 0.8 |  | active current limit curve (VDL2), point 3: voltage (pu)
REECCU1 | CON39 | Ip3 | 1.1 |  | active current limit curve (VDL2), point 3: current limit (pu)
REECCU1 | CON40 | Vp4 | 1.2 |  | active current limit curve (VDL2), point 4: voltage (pu)
REECCU1 | CON41 | Ip4 | 1.1 |  | active current limit curve (VDL2), point 4: current limit (pu)
REECCU1 | CON42 | T | 14400 |  | battery discharge time at rated power (s)
REECCU1 | CON43 | SOCini | 0.5 |  | initial state of charge (pu)
REECCU1 | CON44 | SOCmax | 1 |  | state of charge, upper limit (pu)
REECCU1 | CON45 | SOCmin | 0 |  | state of charge, lower limit (pu)
REECDU1 -- electrical control REEC_D: PV, BESS, WT4 (10-point VDL curves, current compensation)
REECDU1 | ICON1 | PFFLAG | 0 |  | 1 constant power factor, 0 Q control
REECDU1 | ICON2 | VFLAG | 0 |  | 1 voltage loop (Kvp, Kvi) after the Q loop, 0 Q loop only
REECDU1 | ICON3 | QFLAG | 0 |  | 1 voltage / Q control, 0 constant power factor or Q
REECDU1 | ICON4 | PFLAG | 0 |  | 1 P reference times speed (wind)
REECDU1 | ICON5 | PQFLAG | 0 |  | at the current limit: 0 Q priority, 1 P priority
REECDU1 | ICON6 | VCMPFLAG | 0 |  | 1 current compensation (Rc, Xc), 0 reactive droop (Kc)
REECDU1 | CON1 | Vdip | 0.9 |  | voltage below which the dip logic acts (pu)
REECDU1 | CON2 | Vup | 1.1 |  | voltage above which the dip logic acts (pu)
REECDU1 | CON3 | Trv | 0.02 |  | terminal voltage filter time constant (s)
REECDU1 | CON4 | dbd1 | -0.05 |  | deadband, lower edge (pu, 0 or less)
REECDU1 | CON5 | dbd2 | 0.05 |  | deadband, upper edge (pu, 0 or more)
REECDU1 | CON6 | Kqv | 2 |  | reactive current injection gain in a dip (pu/pu)
REECDU1 | CON7 | Iqh1 | 1.05 |  | reactive current injection, upper limit (pu)
REECDU1 | CON8 | Iql1 | -1.05 |  | reactive current injection, lower limit (pu)
REECDU1 | CON9 | Vref0 | 0 |  | reference voltage for the injection (pu; 0 = the initial terminal voltage)
REECDU1 | CON10 | Iqfrz | 0 |  | reactive current held after a dip (pu)
REECDU1 | CON11 | Thld | 0 |  | time the injection is held after a dip (s)
REECDU1 | CON12 | Thld2 | 0 |  | time the active current limit is held after a dip (s)
REECDU1 | CON13 | Tp | 0.02 |  | active power measurement filter time constant (s)
REECDU1 | CON14 | QMax | 0.4 | auto | Q limit, upper (pu on MBASE)
REECDU1 | CON15 | QMin | -0.4 | auto | Q limit, lower (pu on MBASE)
REECDU1 | CON16 | VMAX | 1.1 |  | voltage control limit, upper (pu)
REECDU1 | CON17 | VMIN | 0.9 |  | voltage control limit, lower (pu)
REECDU1 | CON18 | Kqp | 0 |  | Q loop proportional gain
REECDU1 | CON19 | Kqi | 0.1 |  | Q loop integral gain
REECDU1 | CON20 | Kvp | 0 |  | voltage loop proportional gain
REECDU1 | CON21 | Kvi | 40 |  | voltage loop integral gain
REECDU1 | CON22 | Vref1 | 0 |  | voltage reference with VFLAG 0 (pu)
REECDU1 | CON23 | Tiq | 0.02 |  | reactive current command time constant (s)
REECDU1 | CON24 | dPmax | 99 |  | P reference ramp up (pu/s)
REECDU1 | CON25 | dPmin | -99 |  | P reference ramp down (pu/s)
REECDU1 | CON26 | PMAX | 1 | auto | P limit, upper (pu on MBASE)
REECDU1 | CON27 | PMIN | 0 | auto | P limit, lower (pu on MBASE; negative: charging)
REECDU1 | CON28 | Imax | 1.1 |  | converter current limit (pu on MBASE)
REECDU1 | CON29 | Tpord | 0.02 |  | P order filter time constant (s)
REECDU1 | CON30 | Vq1 | 0 |  | reactive current limit curve (VDL1), point 1: voltage (pu)
REECDU1 | CON31 | Iq1 | 1.1 |  | reactive current limit curve (VDL1), point 1: current limit (pu)
REECDU1 | CON32 | Vq2 | 0.3 |  | reactive current limit curve (VDL1), point 2: voltage (pu)
REECDU1 | CON33 | Iq2 | 1.1 |  | reactive current limit curve (VDL1), point 2: current limit (pu)
REECDU1 | CON34 | Vq3 | 0.4 |  | reactive current limit curve (VDL1), point 3: voltage (pu)
REECDU1 | CON35 | Iq3 | 1.1 |  | reactive current limit curve (VDL1), point 3: current limit (pu)
REECDU1 | CON36 | Vq4 | 0.6 |  | reactive current limit curve (VDL1), point 4: voltage (pu)
REECDU1 | CON37 | Iq4 | 1.1 |  | reactive current limit curve (VDL1), point 4: current limit (pu)
REECDU1 | CON38 | Vq5 | 0.8 |  | reactive current limit curve (VDL1), point 5: voltage (pu)
REECDU1 | CON39 | Iq5 | 1.1 |  | reactive current limit curve (VDL1), point 5: current limit (pu)
REECDU1 | CON40 | Vq6 | 0.9 |  | reactive current limit curve (VDL1), point 6: voltage (pu)
REECDU1 | CON41 | Iq6 | 1.1 |  | reactive current limit curve (VDL1), point 6: current limit (pu)
REECDU1 | CON42 | Vq7 | 1 |  | reactive current limit curve (VDL1), point 7: voltage (pu)
REECDU1 | CON43 | Iq7 | 1.1 |  | reactive current limit curve (VDL1), point 7: current limit (pu)
REECDU1 | CON44 | Vq8 | 1.1 |  | reactive current limit curve (VDL1), point 8: voltage (pu)
REECDU1 | CON45 | Iq8 | 1.1 |  | reactive current limit curve (VDL1), point 8: current limit (pu)
REECDU1 | CON46 | Vq9 | 1.2 |  | reactive current limit curve (VDL1), point 9: voltage (pu)
REECDU1 | CON47 | Iq9 | 1.1 |  | reactive current limit curve (VDL1), point 9: current limit (pu)
REECDU1 | CON48 | Vq10 | 1.45 |  | reactive current limit curve (VDL1), point 10: voltage (pu)
REECDU1 | CON49 | Iq10 | 1.1 |  | reactive current limit curve (VDL1), point 10: current limit (pu)
REECDU1 | CON50 | Vp1 | 0 |  | active current limit curve (VDL2), point 1: voltage (pu)
REECDU1 | CON51 | Ip1 | 1.1 |  | active current limit curve (VDL2), point 1: current limit (pu)
REECDU1 | CON52 | Vp2 | 0.3 |  | active current limit curve (VDL2), point 2: voltage (pu)
REECDU1 | CON53 | Ip2 | 1.1 |  | active current limit curve (VDL2), point 2: current limit (pu)
REECDU1 | CON54 | Vp3 | 0.4 |  | active current limit curve (VDL2), point 3: voltage (pu)
REECDU1 | CON55 | Ip3 | 1.1 |  | active current limit curve (VDL2), point 3: current limit (pu)
REECDU1 | CON56 | Vp4 | 0.6 |  | active current limit curve (VDL2), point 4: voltage (pu)
REECDU1 | CON57 | Ip4 | 1.1 |  | active current limit curve (VDL2), point 4: current limit (pu)
REECDU1 | CON58 | Vp5 | 0.7 |  | active current limit curve (VDL2), point 5: voltage (pu)
REECDU1 | CON59 | Ip5 | 1.1 |  | active current limit curve (VDL2), point 5: current limit (pu)
REECDU1 | CON60 | Vp6 | 0.9 |  | active current limit curve (VDL2), point 6: voltage (pu)
REECDU1 | CON61 | Ip6 | 1.1 |  | active current limit curve (VDL2), point 6: current limit (pu)
REECDU1 | CON62 | Vp7 | 1 |  | active current limit curve (VDL2), point 7: voltage (pu)
REECDU1 | CON63 | Ip7 | 1.1 |  | active current limit curve (VDL2), point 7: current limit (pu)
REECDU1 | CON64 | Vp8 | 1.1 |  | active current limit curve (VDL2), point 8: voltage (pu)
REECDU1 | CON65 | Ip8 | 1.1 |  | active current limit curve (VDL2), point 8: current limit (pu)
REECDU1 | CON66 | Vp9 | 1.2 |  | active current limit curve (VDL2), point 9: voltage (pu)
REECDU1 | CON67 | Ip9 | 1.1 |  | active current limit curve (VDL2), point 9: current limit (pu)
REECDU1 | CON68 | Vp10 | 1.45 |  | active current limit curve (VDL2), point 10: voltage (pu)
REECDU1 | CON69 | Ip10 | 1.1 |  | active current limit curve (VDL2), point 10: current limit (pu)
REECDU1 | CON70 | Rc | 0 |  | current / line drop compensation resistance (pu)
REECDU1 | CON71 | Xc | 0 |  | current / line drop compensation reactance (pu)
REECDU1 | CON72 | Tr1 | 0 |  | compensated voltage filter time constant (s)
REECDU1 | CON73 | Kc | 0 |  | reactive droop gain
REECDU1 | CON74 | Ke | 0 | auto | lower active current limit scaling: 0 no charging, -1 charging as discharging (storage)
REECDU1 | CON75 | Vblkl | 0 |  | voltage below which the inverter blocks (pu)
REECDU1 | CON76 | Vblkh | 1.5 |  | voltage above which the inverter blocks (pu)
REECDU1 | CON77 | Tblk_delay | 0 |  | blocking delay (s)
REPCAU1 -- REPC_A as the WECC user model
REPCAU1 | ICON1 | BUSR |  | auto | regulated bus (0 = the terminal)
REPCAU1 | ICON2 | BUS1 |  | auto | P and Q measured on the branch from this bus
REPCAU1 | ICON3 | BUS2 |  | auto | ... to this bus
REPCAU1 | ICON4 | CKT |  | auto | ... this circuit
REPCAU1 | ICON5 | VCFLAG | 1 |  | 1 voltage control with line drop compensation, 0 reactive droop
REPCAU1 | ICON6 | REFFLAG | 1 |  | 1 voltage control, 0 Q control
REPCAU1 | ICON7 | FFLAG | 1 |  | 1 frequency response on, 0 off
REPCAU1 | CON1 | Tfltr | 0.02 |  | voltage (or Q) measurement filter time constant (s)
REPCAU1 | CON2 | Kp | 1 |  | voltage / Q loop proportional gain
REPCAU1 | CON3 | Ki | 5 |  | voltage / Q loop integral gain
REPCAU1 | CON4 | Tft | 0 |  | lead time constant (s)
REPCAU1 | CON5 | Tfv | 0.075 |  | lag time constant (s)
REPCAU1 | CON6 | Vfrz | 0.7 |  | voltage below which the controller freezes (pu)
REPCAU1 | CON7 | Rc | 0 |  | current / line drop compensation resistance (pu)
REPCAU1 | CON8 | Xc | 0 |  | current / line drop compensation reactance (pu)
REPCAU1 | CON9 | Kc | 0 |  | reactive droop gain
REPCAU1 | CON10 | emax | 0.1 |  | error limit, upper (pu)
REPCAU1 | CON11 | emin | -0.1 |  | error limit, lower (pu)
REPCAU1 | CON12 | dbd1 | 0 |  | deadband, lower edge (pu, 0 or less)
REPCAU1 | CON13 | dbd2 | 0 |  | deadband, upper edge (pu, 0 or more)
REPCAU1 | CON14 | Qmax | 0.4 | auto | Q command limit, upper (pu)
REPCAU1 | CON15 | Qmin | -0.4 | auto | Q command limit, lower (pu)
REPCAU1 | CON16 | Kpg | 0.1 |  | frequency (P) loop proportional gain
REPCAU1 | CON17 | Kig | 0.05 |  | frequency (P) loop integral gain
REPCAU1 | CON18 | Tp | 0.25 |  | active power measurement filter time constant (s)
REPCAU1 | CON19 | fdbd1 | -0.0006 |  | frequency deadband, lower edge (pu)
REPCAU1 | CON20 | fdbd2 | 0.0006 |  | frequency deadband, upper edge (pu)
REPCAU1 | CON21 | femax | 999 |  | frequency error limit, upper (pu)
REPCAU1 | CON22 | femin | -999 |  | frequency error limit, lower (pu)
REPCAU1 | CON23 | Pmax | 1 | auto | P command limit, upper (pu)
REPCAU1 | CON24 | Pmin | 0 | auto | P command limit, lower (pu)
REPCAU1 | CON25 | Tlag | 0.1 |  | P command lag time constant (s)
REPCAU1 | CON26 | Ddn | 20 |  | droop gain, over-frequency (pu P / pu f)
REPCAU1 | CON27 | Dup | 0 | auto | droop gain, under-frequency (pu P / pu f)
REAX4BU1 -- REPC_B's auxiliary model on each generator: its share of the plant's P and Q
REAX4BU1 | ICON1 | PCBUS |  | auto | the plant controller's (PLNTBU1's) bus
REAX4BU1 | CON1 | CON1 | 0 |  | reserved
REAX4BU1 | CON2 | Kz | 1 | auto | its share of the plant's Q command
REAX4BU1 | CON3 | Kw | 1 | auto | its share of the plant's P command
REAX4BU1 | CON4 | Qmax | 0.4 | auto | Q command limit, upper (pu)
REAX4BU1 | CON5 | Qmin | -0.4 | auto | Q command limit, lower (pu)
REAX4BU1 | CON6 | Pmax | 1 | auto | P command limit, upper (pu)
REAX4BU1 | CON7 | Pmin | 0 | auto | P command limit, lower (pu)
PLNTBU1 -- plant controller REPC_B, one for the whole plant at the POI (Plant controller REPC_B)
PLNTBU1 | ICON1 | BUSR |  | auto | regulated bus (0 = the terminal)
PLNTBU1 | ICON2 | BUS1 |  | auto | P and Q measured on the branch from this bus
PLNTBU1 | ICON3 | BUS2 |  | auto | ... to this bus
PLNTBU1 | ICON4 | CKT |  | auto | ... this circuit
PLNTBU1 | ICON5 | VCFLAG | 1 |  | 1 voltage control with line drop compensation, 0 reactive droop
PLNTBU1 | ICON6 | REFFLAG | 1 |  | 1 voltage control, 0 Q control
PLNTBU1 | ICON7 | FFLAG | 1 |  | 1 frequency response on, 0 off
PLNTBU1 | CON1 | Tfltr | 0.02 |  | voltage (or Q) measurement filter time constant (s)
PLNTBU1 | CON2 | Kp | 1 |  | voltage / Q loop proportional gain
PLNTBU1 | CON3 | Ki | 5 |  | voltage / Q loop integral gain
PLNTBU1 | CON4 | Tft | 0 |  | lead time constant (s)
PLNTBU1 | CON5 | Tfv | 0.075 |  | lag time constant (s)
PLNTBU1 | CON6 | Vfrz | 0.7 |  | voltage below which the controller freezes (pu)
PLNTBU1 | CON7 | Rc | 0 |  | current / line drop compensation resistance (pu)
PLNTBU1 | CON8 | Xc | 0 |  | current / line drop compensation reactance (pu)
PLNTBU1 | CON9 | Kc | 0 |  | reactive droop gain
PLNTBU1 | CON10 | emax | 0.1 |  | error limit, upper (pu)
PLNTBU1 | CON11 | emin | -0.1 |  | error limit, lower (pu)
PLNTBU1 | CON12 | dbd1 | 0 |  | deadband, lower edge (pu, 0 or less)
PLNTBU1 | CON13 | dbd2 | 0 |  | deadband, upper edge (pu, 0 or more)
PLNTBU1 | CON14 | Qmax | 0.4 | auto | Q command limit, upper (pu)
PLNTBU1 | CON15 | Qmin | -0.4 | auto | Q command limit, lower (pu)
PLNTBU1 | CON16 | Kpg | 0.1 |  | frequency (P) loop proportional gain
PLNTBU1 | CON17 | Kig | 0.05 |  | frequency (P) loop integral gain
PLNTBU1 | CON18 | Tp | 0.25 |  | active power measurement filter time constant (s)
PLNTBU1 | CON19 | fdbd1 | -0.0006 |  | frequency deadband, lower edge (pu)
PLNTBU1 | CON20 | fdbd2 | 0.0006 |  | frequency deadband, upper edge (pu)
PLNTBU1 | CON21 | femax | 999 |  | frequency error limit, upper (pu)
PLNTBU1 | CON22 | femin | -999 |  | frequency error limit, lower (pu)
PLNTBU1 | CON23 | Pmax | 1 | auto | P command limit, upper (pu)
PLNTBU1 | CON24 | Pmin | 0 | auto | P command limit, lower (pu)
PLNTBU1 | CON25 | Tlag | 0.1 |  | P command lag time constant (s)
PLNTBU1 | CON26 | Ddn | 20 |  | droop gain, over-frequency (pu P / pu f)
PLNTBU1 | CON27 | Dup | 0 | auto | droop gain, under-frequency (pu P / pu f)
PLNTBU1 | CON28 | MVAbase | 100 | auto | the plant controller's MVA base
WTDTA1 -- WT3 drive train
WTDTA1 | CON1 | H | 3 |  | inertia constant (s; 0 = infinite bus)
WTDTA1 | CON2 | DAMP | 0 |  | drive train damping (pu)
WTDTA1 | CON3 | Htfrac | 0.92 |  | turbine's share of the inertia
WTDTA1 | CON4 | Freq1 | 1.8 |  | first shaft torsional frequency (Hz)
WTDTA1 | CON5 | Dshaft | 1.5 |  | shaft damping (pu)
WTARA1 -- WT3 aerodynamics
WTARA1 | CON1 | Ka | 0.007 |  | aerodynamic gain
WTARA1 | CON2 | Theta0 | 0 |  | initial pitch angle (deg)
WTPTA1 -- WT3 pitch control
WTPTA1 | CON1 | Kiw | 25 |  | pitch control integral gain (speed)
WTPTA1 | CON2 | Kpw | 150 |  | pitch control proportional gain (speed)
WTPTA1 | CON3 | Kic | 30 |  | pitch compensation integral gain
WTPTA1 | CON4 | Kpc | 3 |  | pitch compensation proportional gain
WTPTA1 | CON5 | Kcc | 0 |  | pitch compensation cross gain
WTPTA1 | CON6 | Tp | 0.3 |  | active power measurement filter time constant (s)
WTPTA1 | CON7 | TetaMax | 27 |  | pitch angle, upper (deg)
WTPTA1 | CON8 | TetaMin | 0 |  | pitch angle, lower (deg)
WTPTA1 | CON9 | RTetaMax | 10 |  | pitch rate, upper (deg/s)
WTPTA1 | CON10 | RTetaMin | -10 |  | pitch rate, lower (deg/s)
WTTQA1 -- WT3 torque control
WTTQA1 | ICON1 | TFLAG | 0 |  | 1 speed reference from power, 0 torque
WTTQA1 | CON1 | Kpp | 3 |  | torque control proportional gain
WTTQA1 | CON2 | Kip | 0.6 |  | torque control integral gain
WTTQA1 | CON3 | Tp | 0.05 |  | active power measurement filter time constant (s)
WTTQA1 | CON4 | Twref | 60 |  | speed reference time constant (s)
WTTQA1 | CON5 | Temax | 1.2 |  | electrical torque, upper (pu)
WTTQA1 | CON6 | Temin | 0 |  | electrical torque, lower (pu)
WTTQA1 | CON7 | p1 | 0.2 |  | power-speed curve, point 1: power (pu)
WTTQA1 | CON8 | spd1 | 0.58 |  | power-speed curve, point 1: speed (pu)
WTTQA1 | CON9 | p2 | 0.4 |  | power-speed curve, point 2: power (pu)
WTTQA1 | CON10 | spd2 | 0.72 |  | power-speed curve, point 2: speed (pu)
WTTQA1 | CON11 | p3 | 0.6 |  | power-speed curve, point 3: power (pu)
WTTQA1 | CON12 | spd3 | 0.86 |  | power-speed curve, point 3: speed (pu)
WTTQA1 | CON13 | p4 | 0.8 |  | power-speed curve, point 4: power (pu)
WTTQA1 | CON14 | spd4 | 1 |  | power-speed curve, point 4: speed (pu)
WTTQA1 | CON15 | TRATE | 0 | auto | turbine rating (MW)
GENROU -- synchronous machine, round rotor (type SYNC)
GENROU | CON1 | Tdop | 6 |  | T'do (s)
GENROU | CON2 | Tdopp | 0.05 |  | T''do (s)
GENROU | CON3 | Tqop | 0.75 |  | T'qo (s)
GENROU | CON4 | Tqopp | 0.07 |  | T''qo (s)
GENROU | CON5 | H | 4 |  | inertia constant (s; 0 = infinite bus)
GENROU | CON6 | D | 0 |  | damping (pu)
GENROU | CON7 | Xd | 1.8 |  | Xd (pu)
GENROU | CON8 | Xq | 1.75 |  | Xq (pu)
GENROU | CON9 | Xdp | 0.3 |  | X'd (pu)
GENROU | CON10 | Xqp | 0.55 |  | X'q (pu)
GENROU | CON11 | Xdpp | 0.25 |  | X''d = X''q (pu)
GENROU | CON12 | Xl | 0.15 |  | leakage reactance (pu)
GENROU | CON13 | S1 | 0.1 |  | saturation at 1.0 pu
GENROU | CON14 | S12 | 0.3 |  | saturation at 1.2 pu
SEXS -- simplified excitation system (type SYNC)
SEXS | CON1 | TA_TB | 0.1 |  | TA / TB
SEXS | CON2 | TB | 10 |  | TB (s)
SEXS | CON3 | K | 100 |  | exciter gain
SEXS | CON4 | TE | 0.05 |  | TE (s)
SEXS | CON5 | EMIN | 0 |  | field voltage, lower (pu)
SEXS | CON6 | EMAX | 5 |  | field voltage, upper (pu)
TGOV1 -- steam turbine-governor (type SYNC)
TGOV1 | CON1 | R | 0.05 |  | droop (pu)
TGOV1 | CON2 | T1 | 0.5 |  | T1 (s)
TGOV1 | CON3 | VMAX | 1.05 | auto | voltage control limit, upper (pu)
TGOV1 | CON4 | VMIN | 0 |  | voltage control limit, lower (pu)
TGOV1 | CON5 | T2 | 1 |  | T2 (s)
TGOV1 | CON6 | T3 | 1 |  | T3 (s)
TGOV1 | CON7 | Dt | 0 |  | turbine damping (pu)